HPC Temperature Monitoring System

Hardware Module

SRS Reference Document

Role: Hardware & Sensor Integration

Controller: ESP32 DevKit V1 (ESP-WROOM-32)

Sensors: DHT11 (Exhaust, GPIO 21)  |  DHT22 (Intake, GPIO 22)

Backend: Supabase REST API (PostgreSQL)

Document Sections

1. Setup Guide   2. Diagrams & Figures   3. References   4. Credentials

Weeks 1 – 13  |  Academic Year 2024–25

Confidential — Internal Use Only

# Table of Contents

Table of Contents	2

1  Hardware Setup Guide — Running from Scratch	3

1.1  Prerequisites — Hardware Components Required	3

1.2  Software Installation	3

1.3  Required Arduino Libraries	3

1.4  Physical Wiring & Pin Assignment	4

1.5  LAN Cable Extension for HPC Room Deployment	4

1.6  Wi-Fi Credentials Configuration (wifi_config.h)	4

1.7  Flashing the Firmware	5

1.8  Verification via Serial Monitor	5

1.9  Common Issues & Troubleshooting	5

2  Diagrams & Figures for SRS / IEEE Documentation	7

2.1  Figure 1 — Wokwi Simulation Environment	7

2.2  Figure 2 — Breadboard Prototype	7

2.3  Figure 3 — Final System with 3D-Printed Enclosures	8

2.4  Figure Placement Summary	9

2.5  Figure 4 — RGB LED Threshold State Logic	9

2.6  Figure 5 — Sensor Drift Calibration Data	10

2.7  Figure 6 — Firmware Timing Architecture	10

3  References	11

3.1  Controller & Development Board	11

3.2  Temperature & Humidity Sensors	11

3.3  Display & Visual Indicators	11

3.4  Wiring & Cable Extension	12

3.5  Procurement Sources	12

3.6  Development Tools & Simulation	12

4  Credentials & Configuration Reference	14

4.1  Wi-Fi Configuration (wifi_config.h)	14

4.2  Supabase Credentials (Used Read-Only in Firmware)	14

4.3  Sensor UUIDs (Assigned in Supabase Database)	14

4.4  LED Threshold Defaults (Firmware Fallback Values)	15

4.5  Key Firmware Constants (Hardware-Owned)	15

# 1  Hardware Setup Guide — Running from Scratch

This section documents every step required to set up, wire, flash, and verify the ESP32-based hardware module of the HPC Temperature Monitoring System on a completely fresh machine. Steps must be followed in order. The firmware files required are Main.ino and wifi_config.h.

## 1.1  Prerequisites — Hardware Components Required

| Component | Specification / Notes |
| --- | --- |
| ESP32 DevKit V1 | ESP-WROOM-32 module, 30 GPIO pins, dual-core, built-in Wi-Fi & Bluetooth |
| DHT11 Module | 3-pin breakout, onboard 10 kΩ pull-up, GPIO 21, cooler Exhaust position |
| DHT22 (AM2302) | 4-pin, ±0.5°C accuracy, external 10 kΩ pull-up required, GPIO 22, Intake position |
| 16x2 LCD I2C | I2C backpack, address 0x27, SDA→GPIO 13, SCL→GPIO 14, backlit |
| RGB LED | Common-cathode, Red→GPIO 25, Green→GPIO 26, Blue→GPIO 27, 220Ω per channel |
| 10 kΩ Resistor | DHT22 DATA line pull-up — placed at sensor end of LAN cable |
| 220 Ω Resistors | Three required — one per RGB LED colour channel |
| Cat5e LAN Cable | For HPC room: extends sensors, display, LED with EMI rejection via twisted pairs |
| Power Supply | 5V / 2A USB adapter + quality Micro-USB cable (not charge-only) |
| Computer | Windows / macOS / Linux with USB port and internet access |

## 1.2  Software Installation

| 1 | Download & Install Arduino IDE 2.x Get the latest release from https://www.arduino.cc/en/software — install for your OS. Launch once to initialise the preferences folder. |
| --- | --- |
| 2 | Add ESP32 Board Support URL Arduino IDE → File → Preferences. In Additional Boards Manager URLs paste: https://raw.githubusercontent.com/espressif/arduino-esp32/gh-pages/package_esp32_index.json |
| 3 | Install ESP32 Package Tools → Board → Boards Manager. Search esp32 by Espressif Systems. Install version 2.x or later. |
| 4 | Select Board & Port Tools → Board → ESP32 Arduino → DOIT ESP32 DEVKIT V1. Tools → Port → select the COM port shown when ESP32 is plugged in. If not detected, install the CP2102 or CH340 USB-to-serial driver. |
| 5 | Open Project Files Place Main.ino and wifi_config.h in the same folder (folder name must match the .ino filename). Open Main.ino in the IDE. |

## 1.3  Required Arduino Libraries

| Library | Author | Install Method | Used For |
| --- | --- | --- | --- |
| DHT sensor library | Adafruit | Library Manager search | All sensor reading code |
| LiquidCrystal I2C | Frank de Brabander | Library Manager search | All LCD output code |
| ArduinoJson | Benoit Blanchon | Library Manager — install v7.x | fetchThresholds() JSON parsing |
| esp_eap_client | ESP-IDF (built-in) | No install — part of ESP32 core | WPA2-Enterprise Wi-Fi |
| WiFi.h | ESP32 Arduino core | No install — part of ESP32 core | Wi-Fi connection |
| HTTPClient.h | ESP32 Arduino core | No install — part of ESP32 core | Supabase HTTP POST / GET |

## 1.4  Physical Wiring & Pin Assignment

Wire all components as follows. For bench testing use breadboard + jumper wires. For HPC room deployment replace with Cat5e LAN cable (see section 1.5).

| ESP32 Pin | Signal | Notes |
| --- | --- | --- |
| GPIO 21 | DHT11 DATA (Exhaust) | 3-pin module — onboard pull-up, no external resistor needed |
| GPIO 22 | DHT22 DATA (Intake) | External 10 kΩ pull-up between DATA and 3.3V required |
| GPIO 13 | LCD SDA (I2C) | Wire.begin(13, 14) in firmware setup() |
| GPIO 14 | LCD SCL (I2C) | Wire.begin(13, 14) in firmware setup() |
| GPIO 25 | RGB LED Red | PWM channel 0 — 220Ω series resistor |
| GPIO 26 | RGB LED Green | PWM channel 1 — 220Ω series resistor |
| GPIO 27 | RGB LED Blue | PWM channel 2 — 220Ω series resistor |
| 3.3V/ VIN / GND | All sensors power & ground | All sensors run on 3.3V and VIN rail |

## 1.5  LAN Cable Extension for HPC Room Deployment

Standard jumper wires are unshielded and susceptible to EMI from HPC room servers and power supplies. A Cat5e LAN cable was used — its twisted pairs provide passive common-mode EMI rejection with no extra components.

| Pair | Wire Colours | Signal | Rationale |
| --- | --- | --- | --- |
| Pair 1 | Orange / Orange-White | DHT11 DATA + GND | Twisted pair isolates data signal from noise |
| Pair 2 | Green / Green-White | DHT22 DATA + GND | Separate pair prevents inter-sensor cross-talk |
| Pair 3 | Brown / Brown-White | 3.3V VCC + GND | Shared power rail |
| Pair 4 | Blue / Blue-White | LCD SDA + SCL (I2C) | Twisted pair suits I2C differential noise rejection |

Note: Pull-up resistors for DHT22 are placed at the sensor end of the cable to compensate for the added capacitance of the extended run.

## 1.6  Wi-Fi Credentials Configuration (wifi_config.h)

The university network uses WPA2-Enterprise authentication requiring three fields: SSID, username, and password. These are stored in a separate wifi_config.h file to isolate credentials from application logic.

#ifndef WIFI_CONFIG_H

#define WIFI_CONFIG_H

const char* WIFI_SSID     = "STUDENT";       // University network SSID

const char* WIFI_USERNAME = "2300001530";     // Institutional username

const char* WIFI_PASSWORD = "";               // Enter password here

#endif

Only authorised university staff should enter the institutional password. Never commit wifi_config.h to any public or private repository.

## 1.7  Flashing the Firmware

| 1 | Place files in same folder Main.ino and wifi_config.h must both be in a folder named identically to the .ino file. |
| --- | --- |
| 2 | Open Main.ino in Arduino IDE File → Open → navigate to the folder → select Main.ino. |
| 3 | Fill in wifi_config.h Open the wifi_config.h tab in the IDE, enter WIFI_SSID, WIFI_USERNAME, WIFI_PASSWORD. Save the file. |
| 4 | Click Upload (→) IDE compiles then uploads. If upload fails immediately, hold the BOOT button on the ESP32 while clicking Upload, release after 'Connecting...' appears. |
| 5 | Wait for 'Done uploading' Upload takes 10–30 seconds. Do not disconnect the board during upload. |

## 1.8  Verification via Serial Monitor

Open Tools → Serial Monitor. Set baud rate to 115200. The following output confirms correct operation:

| Event | Expected Serial Output | Meaning |
| --- | --- | --- |
| Boot | {"event":"boot","detail":"HPC Monitoring System Starting"} | System started correctly |
| Wi-Fi | [WIFI] Connected! IP: x.x.x.x | Network connected |
| Thresholds | [THRESHOLD] Red threshold updated -> 35.0°C | Supabase fetch successful |
| Sensor read | [DHT11] Temp: 23.4°C ¦ Humidity: 48.0% | Every 2 seconds |
| POST success | [HTTP] Response code: 201 | Every 10 seconds |
| LED / LCD | Green LED solid, LCD shows Temp: 23.4°C | Normal range state |

## 1.9  Common Issues & Troubleshooting

| Problem | Solution |
| --- | --- |
| ESP32 not detected | Install CP2102 or CH340 USB-to-serial driver. Try a data-capable Micro-USB cable. |
| Upload fails | Hold BOOT button during upload. Verify correct board and COM port selected. |
| Sensor returns NaN | DHT22: verify 10 kΩ pull-up between DATA and 3.3V at sensor end of cable. Check wire continuity. |
| LCD blank or garbled | Verify I2C address is 0x27. Run an I2C scanner sketch. Check SDA→GPIO 13, SCL→GPIO 14. |
| LED / LCD flickering | Loose solder joint on shared GND. Re-solder all GND joints and secure with heat shrink tubing. |
| Wi-Fi not connecting | Check wifi_config.h credentials. For hotspot: enable Maximize Compatibility (forces 2.4GHz). |
| Thresholds not updating | Verify Supabase API key in Main.ino. Confirm led_thresholds table exists in Supabase project. |
| HTTP 401 / 403 error | Supabase API key mismatch — copy the anon key from Supabase project settings. |

# 2  Diagrams & Figures for SRS / IEEE Documentation

This section contains all visual assets from the hardware module with actual photographs and screenshots embedded. Each figure includes a description and SRS placement guidance. Three hardware phases are shown: simulation, breadboard prototype, and final deployed system.

Phase 1 — Virtual Simulation (Wokwi.com)

## 2.1  Figure 1 — Wokwi Simulation Environment

| SRS Placement | Hardware Architecture / System Overview / Prototyping Methodology |
| --- | --- |
| Description | The Wokwi browser-based ESP32 simulation showing the full virtual circuit: ESP32 DevKit V1, DHT22 sensor, 16x2 LCD display, and RGB LED with pull-up resistors. The code panel shows DHT, Wire, and LiquidCrystal_I2C library includes, with GPIO 13/14 (I2C) and GPIO 25/26/27 (PWM) configured. Demonstrates firmware logic validated in a risk-free environment before any physical hardware was connected. |
| IEEE Relevance | Supports the prototyping approach rationale in the system design section. |

Figure 1 — Wokwi.com simulation: ESP32 DevKit V1 with DHT22, 16x2 LCD, RGB LED, and pull-up resistors. Firmware visible on left.

Phase 2 — Physical Breadboard Prototype

## 2.2  Figure 2 — Breadboard Prototype

| SRS Placement | Hardware Implementation / Bench Validation / Physical Circuit Assembly |
| --- | --- |
| Description | The physical breadboard prototype showing the ESP32 DevKit V1 connected to the DHT sensor, 16x2 LCD displaying live readings (Temp: 23.4°C / Humi: 48.4%), and the full system operating during bench validation. Confirms physical hardware behaviour matches the Wokwi simulation, with sensor readings visible on LCD and Supabase POST confirmed via Serial Monitor. |
| IEEE Relevance | Documents the hardware validation milestone before LAN cable deployment. |

Figure 2 — Breadboard prototype: ESP32 + DHT sensor, 16x2 LCD showing Temp: 23.4°C / Humi: 48.4%. Full system live — bench validation phase.

Phase 3 — Final Deployed System (Production)

## 2.3  Figure 3 — Final System with 3D-Printed Enclosures

| SRS Placement | Physical Deployment / Enclosure Design / Final System Description |
| --- | --- |
| Description | The completed production system showing: 3D-printed enclosures for all components, LCD displaying Temp: 22.9°C / Humi: 45.3%, green LED indicating normal operating state, Cat5e LAN cable with twisted-pair terminations (bottom-left), and sensor enclosures. All components fully operational inside enclosures with no signal degradation. This is the system as installed in the HPC room following Prof. Akbulut's approval. |
| IEEE Relevance | Documents the final deliverable state for the implementation section of the SRS. |

Figure 3 — Final deployed system: 3D-printed enclosures, LCD (Temp: 22.9°C / Humi: 45.3%), green LED (normal state), Cat5e LAN cable termination.

## 2.4  Figure Placement Summary

| Figure | Phase | Key Evidence | SRS / IEEE Section |
| --- | --- | --- | --- |
| Fig 1 | Wokwi Simulation | Circuit & firmware validated risk-free | Hardware Architecture / Overview |
| Fig 2 | Breadboard Prototype | Physical hardware matches simulation | Hardware Implementation / Validation |
| Fig 3 | Final Deployed System | Production-ready, enclosures, LAN cable deployed | Physical Deployment / Final System |

## 2.5  Figure 4 — RGB LED Threshold State Logic

| SRS Placement | Functional Requirements — FR-3 Threshold-Based Alerting |
| --- | --- |
| Description | Three LED colour states driven by averaged temperature from both sensors. Thresholds are fetched dynamically from Supabase every 10 seconds with hardcoded fallback defaults (35°C / 18°C) if offline. |

| State | Condition | LED Behaviour | Meaning |
| --- | --- | --- | --- |
| COLD | avgTemp < 18.0°C | Blue — Solid ON | Possible cooling fault / sensor issue |
| NORMAL | 18.0°C ≤ avgTemp ≤ 35.0°C | Green — Solid ON | System within safe operating range |
| WARNING | avgTemp > 35.0°C | Red — Blinking 500ms | Critical overheating alert |

## 2.6  Figure 5 — Sensor Drift Calibration Data

| SRS Placement | Sensor Accuracy / Calibration Results / Hardware Validation |
| --- | --- |
| Description | Drift analysis between DHT11 (±2°C accuracy) and DHT22 (±0.5°C, reference sensor) under four controlled conditions. All values within the ≤2°C acceptable tolerance. |

| Condition | DHT11 Reading | DHT22 Reading | Drift | Result |
| --- | --- | --- | --- | --- |
| Ambient (room temp) | ~24.0°C | ~23.5°C | 0.5°C | ✓ PASS |
| Heat applied (dryer) | ~39.2°C | ~40.1°C | 0.9°C | ✓ PASS |
| Cold applied (fan) | ~16.8°C | ~17.3°C | 0.5°C | ✓ PASS |
| After 24h endurance | ~23.8°C | ~23.4°C | 0.4°C | ✓ PASS |

## 2.7  Figure 6 — Firmware Timing Architecture

All timing tasks use non-blocking millis() logic and run completely independently of each other:

| Constant | Value | Purpose |
| --- | --- | --- |
| READ_INTERVAL | 2 000 ms | Sensor poll (DHT11 + DHT22) + LCD update + LED threshold check |
| SEND_INTERVAL | 10 000 ms | Ring buffer flush → POST to Supabase sensor_readings table |
| BLINK_INTERVAL | 500 ms | Red LED ON/OFF toggle in WARNING state |
| THRESHOLD_INTERVAL | 10 000 ms | GET led_thresholds from Supabase, update threshold variables |
| WIFI_RETRY_BASE | 2 000 ms | Exponential backoff base for Wi-Fi reconnect (doubles up to 64s) |
| HTTP_RETRY_BASE | 1 000 ms | Exponential backoff base for HTTP retry (3 attempts, max 16s) |

# 3  References

All references used during hardware design, physical wiring, firmware development, sensor calibration, and testing. Supabase backend, database schema, and frontend references are outside the hardware module scope.

## 3.1  Controller & Development Board

| Ref | Source & Details |
| --- | --- |
| [R1] | ESP32 DevKit V1 High-Resolution Pinout — Mischianti |
| [R2] | ESP32 Pin Reference — Last Minute Engineers |

[R1] — ESP32 DevKit V1 High-Resolution Pinout — Mischianti

Used to select GPIO 21 (DHT11), GPIO 22 (DHT22), GPIO 13/14 (I2C), and GPIO 25/26/27 (PWM LED).

https://mischianti.org/doit-esp32-dev-kit-v1-high-resolution-pinout-and-specs/

[R2] — ESP32 Pin Reference — Last Minute Engineers

Secondary reference to validate GPIO capabilities, PWM support, and I2C flexibility on non-default pins.

https://lastminuteengineers.com/esp32-pinout-reference/

## 3.2  Temperature & Humidity Sensors

| Ref | Source & Details |
| --- | --- |
| [R3] | DHT11 / DHT22 Complete Guide — Random Nerd Tutorials |
| [R4] | DHT22 (AM2302) Datasheet — AOSONG Electronics |
| [R5] | DHT11 Datasheet |

[R3] — DHT11 / DHT22 Complete Guide — Random Nerd Tutorials

Used for pull-up resistor values, READ_INTERVAL selection (2s minimum for DHT22), NaN handling, and library initialisation.

https://randomnerdtutorials.com/complete-guide-for-dht11dht22-humidity-and-temperature-sensor-with-arduino/

[R4] — DHT22 (AM2302) Datasheet — AOSONG Electronics

Confirms ±0.5°C accuracy, 2s minimum sampling, 4-pin configuration, and 10 kΩ pull-up requirement.

Available via component suppliers / AOSONG Electronics

[R5] — DHT11 Datasheet

Confirms ±2°C accuracy, 1s minimum sampling, and 3-pin module with onboard pull-up resistor.

Available via component suppliers

## 3.3  Display & Visual Indicators

| Ref | Source & Details |
| --- | --- |
| [R6] | LCD 16x2 I2C Datasheet |
| [R7] | RGB LED Module — Trendyol (HW-479) |

[R6] — LCD 16x2 I2C Datasheet

Confirms I2C address 0x27, pin layout, and initialisation used in Wire.begin(13, 14) and LiquidCrystal_I2C lcd(0x27, 16, 2).

https://www.scribd.com/document/487972154/18-DATASHEET-LCD

[R7] — RGB LED Module — Trendyol (HW-479)

Product page confirming common-cathode configuration and forward voltage for resistor calculation.

https://www.trendyol.com/pd/genel-markalar/arduino-hw-479-rgb-led-modulu-p-650491682

## 3.4  Wiring & Cable Extension

| Ref | Source & Details |
| --- | --- |
| [R8] | Cat5e Twisted-Pair EMI Rejection — TIA/EIA-568-B |
| [R9] | I2C Protocol over Extended Cabling — NXP Semiconductors |

[R8] — Cat5e Twisted-Pair EMI Rejection — TIA/EIA-568-B

Twisted pairs provide common-mode EMI rejection critical in HPC room environments with high-frequency switching noise.

TIA/EIA-568-B Telecommunications Standard

[R9] — I2C Protocol over Extended Cabling — NXP Semiconductors

Used to justify twisted-pair routing for SDA/SCL lines in Pair 4 of the LAN cable.

NXP Semiconductors — I2C-bus specification and user manual

## 3.5  Procurement Sources

| Ref | Source & Details |
| --- | --- |
| [R10] | ESP32-WROOM-32 DevKit V1 — Trendyol (Argerobo) |
| [R11] | DHT22 Sensor Module — robo90.com |
| [R12] | 16x2 LCD I2C Module — robo90.com |
| [R13] | 10kΩ Resistor Pack — robo90.com |
| [R14] | Breadboard 830-pin — robo90.com |
| [R15] | 5V 2A USB Power Adapter — PTT AVM (Koodmax) |

[R10] — ESP32-WROOM-32 DevKit V1 — Trendyol (Argerobo)

Controller board.

https://www.trendyol.com/argerobo/esp32-wifi-bluetooth-iot-karti-30-pin-p-1108739956

[R11] — DHT22 Sensor Module — robo90.com

Intake-side temperature sensor.

https://www.robo90.com/dht22-sicaklik-ve-nem-algilama-sensoru

[R12] — 16x2 LCD I2C Module — robo90.com

LCD display.

https://www.robo90.com/16x2-lcd-ekran-i2c-modullu-mavi-arduino-uyumlu

[R13] — 10kΩ Resistor Pack — robo90.com

DHT22 pull-up resistors.

https://www.robo90.com/10k-direnc-paketi-1-4-w-10-adet

[R14] — Breadboard 830-pin — robo90.com

Prototyping base for bench testing.

https://www.robo90.com/elektronik-breadboard-buyuk-boy-830-pin

[R15] — 5V 2A USB Power Adapter — PTT AVM (Koodmax)

ESP32 power supply.

https://www.pttavm.com/koodmax-5v-2a-mini-usb-5-pin-arduino-Icin-guc-kaynagi-adaptor-p282415040

## 3.6  Development Tools & Simulation

| Ref | Source & Details |
| --- | --- |
| [R16] | Wokwi ESP32 Simulator |
| [R17] | Arduino IDE 2.x |
| [R18] | Supabase REST API Documentation |

[R16] — Wokwi ESP32 Simulator

Browser-based simulator used to validate full firmware circuit before connecting physical hardware. Confirmed sensor polling, I2C, and LED PWM logic.

https://wokwi.com/esp32

[R17] — Arduino IDE 2.x

Development environment for firmware compilation and upload to ESP32.

https://www.arduino.cc/en/software

[R18] — Supabase REST API Documentation

Used to implement HTTP POST to sensor_readings and GET from led_thresholds. Documents headers, auth, and JSON payload format.

https://supabase.com/docs/guides/api

# 4  Credentials & Configuration Reference

Scope: This section covers only credentials within the hardware role. Supabase project setup, database schema, RLS policies, and frontend environment variables are owned by the backend and frontend teams respectively.

CONFIDENTIAL — Distribute only to authorised project personnel. Do not commit any credentials to any repository.

## 4.1  Wi-Fi Configuration (wifi_config.h)

The hardware role created wifi_config.h to isolate WPA2-Enterprise credentials from firmware logic. Only the three fields below need updating — no other firmware changes are required.

| File | wifi_config.h (same directory as Main.ino) |
| --- | --- |
| Auth Protocol | WPA2-Enterprise (EAP-PEAP) — requires SSID + username + password |
| WIFI_SSID | "STUDENT" — University WPA2-Enterprise network name (confirmed by Prof. Akbulut) |
| WIFI_USERNAME | "2300001530" — Institutional student ID / username |
| WIFI_PASSWORD | [ To be entered directly on device by authorised university staff only ] |
| Status (Week 13) | SSID and USERNAME confirmed set. PASSWORD entry pending authorised staff access. |
| EAP Functions | esp_eap_client_set_identity() / set_username() / set_password() + esp_wifi_sta_enterprise_enable() |
| Hotspot fallback | iPhone: Settings → Personal Hotspot → Maximize Compatibility (forces 2.4GHz). Use WPA2-Personal mode with WiFi.begin(SSID, password). |

## 4.2  Supabase Credentials (Used Read-Only in Firmware)

These values are hardcoded in Main.ino and were provided by the backend team. The hardware role uses them only to POST sensor readings and GET LED thresholds.

| Project URL | https://ahzocemntuurmqnicrmj.supabase.co |
| --- | --- |
| POST Endpoint | https://ahzocemntuurmqnicrmj.supabase.co/rest/v1/sensor_readings |
| GET Endpoint | https://ahzocemntuurmqnicrmj.supabase.co/rest/v1/led_thresholds |
| API Key (anon) | eyJhbGciOiJIUzI1NiIsInR5cCI6IkpXVCJ9.eyJpc3MiOiJzdXBhYmFzZSIsInJlZiI6ImFoem9jZW1udHV1cm1xbmljcm1qIiwicm9sZSI6ImFub24iLCJpYXQiOjE3NzM3NjU4MzYsImV4cCI6MjA4OTM0MTgzNn0.Y-3KeaN3L6X3n6I4ZKhOcTYVA3O6GcSBl2qiA-VpbIE |
| Auth Headers | apikey: <API_KEY> ¦ Authorization: Bearer <API_KEY> |
| POST Headers | Content-Type: application/json ¦ Prefer: return=minimal |
| Key Type | anon / public JWT — safe for embedded firmware at this project scope |
| Service Role | NOT stored in firmware — owned and managed by backend team only |

The anon key is a public JWT. Row-Level Security (RLS) policies in Supabase control access — managed by the backend team.

## 4.3  Sensor UUIDs (Assigned in Supabase Database)

| DHT11 Sensor UUID | 02952bb9-3804-490c-bf01-ec760a0a21dc |
| --- | --- |
| DHT11 Position | Cooler Exhaust side of HPC rack — measures incoming ambient air temperature |
| DHT11 GPIO | GPIO 21 — 3-pin module, onboard 10 kΩ pull-up |
| DHT22 Sensor UUID | dd0e2f64-129c-4066-a1cb-29f1165ad4a7 |
| DHT22 Position | Intake side of HPC rack — measures outlet air temperature post-processing |
| DHT22 GPIO | GPIO 22 — 4-pin AM2302, external 10 kΩ pull-up at sensor end of cable |

## 4.4  LED Threshold Defaults (Firmware Fallback Values)

If Supabase fetch fails or Wi-Fi is unavailable, these fallback values are used. Live thresholds are fetched from the led_thresholds table every 30 seconds and can be adjusted from the frontend without reflashing.

| thresholdWarnMin (red) | 35.0°C — avgTemp above this triggers blinking red LED (WARNING state) |
| --- | --- |
| thresholdColdMax (blue) | 18.0°C — avgTemp below this triggers solid blue LED (COLD state) |
| Normal / Green range | 18.0°C to 35.0°C — solid green LED, no alert |
| Fetch interval | Every 10 000ms (10s), plus once immediately on boot |
| Fallback behaviour | Defaults used on boot and if any fetch fails — system never crashes or uses undefined values |

## 4.5  Key Firmware Constants (Hardware-Owned)

| Constant | Value | Purpose |
| --- | --- | --- |
| DHT11_PIN | 21 | GPIO — DHT11 data signal |
| DHT22_PIN | 22 | GPIO — DHT22 data signal |
| LCD_ADDRESS | 0x27 | I2C address of LCD backpack |
| I2C SDA / SCL | 13 / 14 | Wire.begin(13, 14) in setup() |
| redPin / greenPin / bluePin | 25/26/27 | PWM output for RGB LED channels |
| PWM Frequency | 5 000 Hz | 8-bit resolution — ledcAttachChannel() |
| READ_INTERVAL | 2 000 ms | Sensor read + LCD update cycle |
| SEND_INTERVAL | 10 000 ms | Supabase POST cycle (ring buffer flush) |
| BLINK_INTERVAL | 500 ms | Red LED blink half-period in WARNING state |
| THRESHOLD_INTERVAL | 10 000 ms | LED threshold re-fetch from Supabase |
| BUFFER_SIZE | 32 | Ring buffer capacity for offline resilience |
| MAX_WIFI_RETRIES | 6 | Max reconnect attempts before reset (backoff 2s → 64s) |
| MAX_HTTP_RETRIES | 3 | Max POST retry attempts (backoff 1s → 16s) |

Hardware module fully verified — Week 13. All test cases TC01–TC11 passed. System demo-ready. Pending: authorised university staff to enter WPA2-Enterprise password into wifi_config.h.